LITTLE COLORADO SANITARY DISTRICT

SOLIDS SEPARATION TANK INSPECTION FORM

(Manual Write-In Form - September 2026)

| NOTICE REGARDING INSPECTION REQUIREMENTS Under Article II, Section 2(D) of the District's Third Amended Rules and Regulations, all Solids Separation Tanks (SSTs) must be inspected every 8 years. Inspections include: (1) Measurement of scum and sludge to determine pumping need; and (2) Structural Integrity Inspection (if tank is pumped). Regardless of sludge/scum findings, a full pumping and structural inspection is required at least every 16 years. Structures with grease traps or interceptors must have their SSTs inspected annually and must include: (1) Measurement of scum and sludge to determine pumping need; and (2) Structural Integrity Inspection (if tank is pumped). Regardless of sludge/scum findings, a full pumping and structural inspection is required at least every 4 years. If pumping is required at an 8-year inspection, or at a 4-year inspection for structures with grease traps or interceptors, the structural inspection must be performed at the same time. Failure to comply may result in enforcement action. |  |
| --- | --- |
| 1. Property Information |  |  |
| Property Address: ________________________________ ________________________________________________ | Tax Parcel No.: _____________________ |  |
| 2. Current Owner Information |  |  |
| Owner Name: _____________________________________________ |  |  |
| 3. Inspector Information |  |  |
| Inspector: ________________________________ | License #: _______________________ |  |
| Company: ________________________________ | Phone: _________________________ |  |
| Email: __________________________________________ |  |  |
| 4. Site and Usage Information |  |  |
| Use: ☐ Residential ☐ Commercial # Tanks: __________________ |  |  |
| Grease Trap? ☐ Yes ☐ No Occupancy: ☐ Full ☐ Seasonal ☐ Intermittent |  |  |
| 5. Tank Inspection & Pumping Information |  |  |
| Date of last inspection: ______________________ | Date of last pumping: _______________________ |  |
| Scum Thickness (SC): | ____________________ inches |  |
| Sludge Thickness (SL): | ____________________ inches |  |
| Liquid Depth (DW): | ____________________ inches |  |

If (SC + SL) / DW > 33%  →  Tank must be pumped.

| Top of scum to top of outlet baffle (SBT) - If <1 inch, pump: ____________ |  |  |
| --- | --- | --- |
| Bottom of scum to bottom of outlet baffle (SBB) - If <3 inches, pump: ____________ |  |  |
| Was the tank pumped? ☐ Yes ☐ No |  |  |
| If No - Reason: ☐ <33% filled ☐ Tank not in operation |  |  |
| Other reason: ____________________________________________________________________________________ ________________________________________________________________________________________________ |  |  |
| 5. Tank Inspection & Pumping Information - Continued |  |  |
| Liquid level: ☐ Normal ☐ Low ☐ High ☐ Unknown |  |  |
| Depth of soil cover over access port: ________________ | Tank riser: ☐ Present ☐ Absent |  |
| Tank Construction: ☐ Metal ☐ Concrete ☐ Fiberglass Other: __________________________ |  |  |
| Compartments: ☐ One ☐ Multiple Capacity (gallons): __________________ |  |  |
| Baffles - Inlet: ☐ Present ☐ Absent Outlet: ☐ Present ☐ Absent |  |  |
| Clean-out on outlet side? ☐ Yes ☐ No Distance: __________________________ |  |  |
| Effluent filter present/cleaned? ☐ Yes ☐ No |  |  |
| Reason if not cleaned: _______________________________________________________________________________ ___________________________________________________________________________________________________ |  |  |
| Home pump station? ☐ Yes ☐ No |  |  |
| Repairs/maintenance performed? ☐ Yes ☐ No |  |  |
| Explain: ___________________________________________________________________________________________ ___________________________________________________________________________________________________ ___________________________________________________________________________________________________ |  |  |
| 5A. Structural Integrity Inspection (requires pumping) |  |  |
| ☐ Tank shell/lid sound ☐ Minor surface issues ☐ Major deterioration |  |
| ☐ Access lids secure and rated for load |  |
| ☐ Inlet baffle intact ☐ Outlet baffle intact ☐ Baffle damage observed |  |
| ☐ Seams/joints intact ☐ Leakage observed |  |
| ☐ No infiltration/exfiltration ☐ Leakage present |  |
| ☐ Site free of stressors (traffic, roots, loading) ☐ Stress observed |  |
| Structural Summary: ☐ Sound ☐ Minor Issues (monitor) ☐ Significant Issues |  |  |
| If Significant Issues: ☐ Repair ☐ Replace |  |  |
| Inspector Notes: ____________________________________________________________________________________ __________________________________________________________________________________________________ __________________________________________________________________________________________________ |  |  |
| 6. Inspection Summary |  |  |
| Is the tank functioning properly until next inspection? ☐ Yes ☐ No |  |  |
| Recommended improvements: ________________________________________________________________________ ___________________________________________________________________________________________________ ___________________________________________________________________________________________________ |  |  |
| 7. Inspector Certification |  |  |

I certify this inspection was completed to the best of my knowledge.

| Inspector's Name: _____________________________ | Date: ________________________________ |
| --- | --- |
| Inspector's Signature: ______________________________ |  |